## Calculation
HSM3105 Worst Case Loop Current Calculator v1.04
Instructions:
Power Mode | High Power-HSM2204 PSU |  |  | Max. 243mA @40V | ← | Select Power mode and program the board accordingly
Custom PSU 12V Output Current [mA] |  |  |  | 1000 |  | If Custom PSU is chosen for power mode, insert the PSU output current
MX Loop Composition
Quantity | Type | Istby[mA] | Inrush Current [mA @40V] | Alarm Current [mA @40V] | ← | Edit the quantity of MX devices according to their type.
0 | MX920 - Isolator | 0 | 0 | 0
0 | MX974 - Wall PIR | 0 | 0 | 0
0 | MX922 - Glass-Break | 0 | 0 | 0
0 | MX862 - Ceiling PIR | 0 | 0 | 0
0 | MX916 - Smoke + Heat | 0 | 0 | 0
0 | MX926 - Smoke | 0 | 0 | 0
0 | MX936 - Heat | 0 | 0 | 0
0 | MX975 - Magnetic Contact | 0 | 0 | 0
0 | MX975-I - Input Contact | 0 | 0 | 0
0
| % Alarmed Devices at same time: |  | 34% |  | ← | Expected percentage of devices with Alarm LED turned ON at the same time
Total Current
| mA @40V |  | mA @12V | Max Loop LOAD
Stby Current | 0 |  | 0 | 0%
Inrush Current | 0 |  | 100 | 0% | ← | If this Load is higher than 100% the loop cannot turn ON
Alarm Current | 0 |  | 100 | 0%
Alarm Current | 0 |  | 100 | 0% | ← | If this Load is higher than 100% the loop could go in overcurrent and consequently shut down
If any of the 2 indicators is higher than 100% the possible actions are:
- Reduce number of loop devices.
- Change the Power Mode for higher current capability
Glossary:
Alarm Current | The current drained by the loop device when this is in Alarm condition with its LED ON
Inrush Current | The Current drained by the loop device when the loop is powered ON
Power Modes | The supply mode of the HSM3105.
When "Low Power" is selected the module is powered by the Panel itself.
When set in "High Power" the module is powered by External PSU
Notes:
Total Current @12V takes in account the HSM3105 board electronics needed current
Refer back to the PSU manual to make sure about the available output current
For MX920 isolator the 16mA current (isolator active) is not part of this spreadsheet calculation since this is triggered by a short circuit fault on the loop.

## Parameters (hidden)
Empty |  | Istby[mA] | Ialm[mA] | Irush[mA] | Notes | Power Mode | Imax@40V[mA] | PSU Imax@12V[mA]
MX975-I - Input Contact | ECNT | 0.2 | 3 | 0.3 | External Input Contact | Low Power | 67 | 348
MX974 - Wall PIR | PIRW | 0.3 | 3.5 | 3 | PIR Wall | High Power-HSM2204 PSU | 243 | 1000
MX922 - Glass-Break | GB | 0.3 | 6 | 3 | Glass Break | High Power-HSM2300 PSU | 243 | 1000
MX862 - Ceiling PIR | PIRC | 0.3 | 3.5 | 3 | PIR Ceiling | High Power-Third Party 1.6A 12V PSU | 400 | 1580
MX916 - Smoke + Heat | PH | 0.35 | 4 | 1.3 | Smoke + Heat Detector | High Power-Custom PSU | 243 | 1000 | Upper limited to 400mA
MX926 - Smoke | P | 0.35 | 4 | 1.3 | Smoke Detector
MX936 - Heat | H | 0.35 | 4 | 1.3 | Heat Detetctor | Other | mA
MX975 - Magnetic Contact | CNT | 0.2 | 3 | 0.3 | Magnetic Contact | HSM3105 Board Drain | 100
MX920 - Isolator | LIM | 0.09 | 0.09 | 1.5 | Line Isolator Module
MX975I - Input Contact | Mim | 0.46 | 4.5 | 1.4 | Mini Input Module